## Sheet1
For premises located at: Hume Highway, Jugiong, NSW.
Licence No. 1723
Activity Type: Miscellaneous Licenced Discharge to Waters (at any time) (91)
Activity Scale: >100 - 1000 Max Annual Volume of Discharge
Unit of measure: ML discharged
A2 Premises to which the licence applies:
Details
Jugiong Water Treatment Plant
Hume Highway
Jugiong
2726
Lot 305 DP 753621
P1 Location of monitoring/discharge points and areas.
EPA identification No. 1
Type of monitoring point: Discharge to waters.
Type of discharge point: Discharge to waters.
Description of location: Concrete pipe 150 metres south
of the Jugiong Water Treatment Plant.
JUGIONG WATER TREATMENT PLANT SLUDGE LAGOON
DISCHARGE TO RIVER
CHARLES STURT UNIVERSITY
Laboratory Analysis Results
Date sample taken | Date report issued | BOD mg/l | TSS mg/l | Estimated Monthly Discharge ML | Daily maximum discharge for the month in kl | EPA REF | Time Sample Collected | Name of collecting officer
2012-03-27 | 2012-04-12 | <2 | <2 |  | 1312 |  | 11:30 | B Ford
2012-04-10 | 2012-04-20 | <2 | 2 |  | 1029 |  | 9:30 | B Ford
2012-05-29 | 2012-06-06 | <2 | <2 |  | 2088 |  | 10:00 | I Basham
2012-06-14 | 2012-06-22 | <2 | <2 |  | 2088 |  | 11:00 | B Ford
2012-07-10 | 2012-07-24 | 2 | 9 |  | 1000 |  | 11:00 | B Ford
2012-08-07 | 2012-08-14 | <2 | <2 |  | 1000 |  | 10:45 | I Basham
2012-09-12 | 2012-09-18 | 3 | 33 |  | 892 | C 04653 | 10:30 | I Basham
2012-09-12 | 2012-09-27 | <2 | <2 |  |  | retest | 15:10 | I Basham
2012-10-16 | 2012-10-24 | <2 | <2 |  | 1281 |  | 14:00 | I Basham
2012-11-12 | 2012-11-15 | <2 | 3 |  | 1281 |  | 10:00 | I Basham
2012-12-06 | 2012-12-14 | <2 | <2 |  | 1281 |  | 11:00 | I Basham
2013-01-13 | 2013-02-08 | <2 | 4 |  | 1826 |  | 10:00 | I Basham
2013-02-13 | 2013-03-05 | <2 | <2 |  | 1281 |  | 9:45 | B Ford
2013-03-13 | 2013-04-03 | <2 | 3 |  | 892 |  | 11:00 | B Ford
2013-04-13 | 2013-04-24 | <2 | <2 |  | 892 |  | 10:45 | B Ford
2013-05-13 | 2013-05-31 | <2 | 3 |  | 3185 |  | 10:30 | I Basham
2013-06-13 | 2013-06-27 | <2 | <1 |  | 2645 |  | 11:00 | I Basham
2013-07-13 | 2013-08-02 | <2 | <2 |  | 892 |  | 10:15 | I Basham
2013-08-08 | 2013-08-15 | <2 | <2 |  | 892 |  | 11:00 | I Basham
2013-09-13 | 2013-10-03 | <2 | <2 |  | 892 |  | 11:00 | I Basham
2013-10-13 | 2013-11-01 | <2 | <2 |  | 2980 |  | 9:30 | B Ford
2013-11-29 | 2013-12-06 | <2 | 2 |  | 1281 |  | 11:30 | I Basham
2013-12-03 | 2013-12-12 | <2 | <2 |  | 2407 |  | 10:00 | B Ford
2014-01-23 | 2014-02-11 | <2 | 2 |  | 2407 |  | 11:00 | I Basham
2014-02-18 | 2014-02-26 | <2 | <2 |  | 2407 |  | 15:00 | I Basham
2014-03-27 | 2014-04-09 | <2 | 3 |  | 1281 |  | 11:00 | R Davis
2014-04-10 | 2014-04-16 | <2 | 4 |  | 892 |  | 15:30 | I Basham
2014-05-27 | 2014-06-03 | <2 | 3 |  | 1281 |  | 11:00 | I Basham
2014-06-23 | 2014-07-01 | <2 | 5 |  | 1281 |  | 11:00 | I Basham
2014-07-23 | 2014-07-31 | <2 | 4 |  | 1281 |  | 10:15 | I Basham
2014-08-18 | 2014-08-25 | <2 | 4 |  | 1281 |  | 9:30 | I Basham
2014-09-22 | 2014-09-30 | <2 | 3 |  | 3281 |  | 11:00 | I Basham
2014-10-28 | 2014-11-04 | <2 | <2 |  | 2892 |  | 12:00 | R Davis
2014-11-24 | 2014-12-05 | <2 | <2 |  | 1826 |  | 1:00 | R Davis
2014-12-08 | 2014-12-19 | <2 | <2 |  | 1826 |  | 11:00 | I Basham
2015-01-23 | 2015-02-03 | <2 | <2 |  | 2407 |  | 12:00 | B Ford
2015-02-27 | 2015-03-06 | <2 | <2 |  | 1826 |  | 12:30 | I Basham
2015-03-25 | 2015-03-02 | <2 | <2 |  | 1826 |  | 10:30 | R Davis
2015-04-27 | 2015-05-05 | 8 | <2 |  | 1281 |  | 10:30 | I Basham
2015-04-27 | 2015-05-19 | <2 | <2 |  |  |  | Retest | I Basham
2015-05-12 | 2015-05-19 | <2 | <2 |  | 1281 |  | 11:00 | I Basham
2015-06-15 | 2015-06-25 | <2 | <2 |  | 1281 |  | 11:00 | B Ford
2015-07-17 | 2015-07-24 | <2 | <2 |  | 1281 |  | 9:30 | I.Basham
2015-08-28 | 2015-09-04 | <2 | <2 |  | 1281 |  | 11:45 | B Ford
2015-09-24 | 2015-09-30 | <2 | <2 |  | 2892 |  | 13:00 | B Ford
23//10/15 | 2015-10-30 | <2 | 6 |  | 2200 |  | 9:00 | I Basham
2015-11-17 | 2015-11-30 | <2 | <2 |  | 1281 |  | 10:00 | B Ford
2015-12-17 | 2015-12-23 | <2 | 3 |  | 1826 |  | 10:45 | R Davis
2016-01-19 | 2016-01-27 | 2 | 24 |  | 1826 |  | 10:30 | I Basham
2016-02-22 | 2016-03-02 | <2 | 10 |  | 1826 |  | 11:00 | I.Basham
2016-04-06 | 2016-04-21 | <2 | <2 |  | 1826 |  | 11:00 | B.Ford
2016-04-26 | 2016-05-06 | <2 | <2 |  | 1281 |  | 10:30 | R.Davis
2016-06-07 | 2016-06-14 | <2 | <2 | 19.246 | 1281 |  | 10:15 | B.Ford
2016-06-20 | 2016-06-27 | <2 | <2 | 19.13 | 2000 |  | 9:20 | R.Davis
2016-07-18 | 2016-07-26 | <2 | <2 | 17.481 | 892 |  | 11:00 | R.Davis
2016-08-15 | 2016-08-23 | <2 | 2 | 19.588 | 2892 |  | 10:30 | R Davis
2016-09-12 | 2016-09-21 | 2 | <2 | 17.099 | 2100 |  | 10:30 | R Davis
2016-10-21 | 2016-10-27 | <2 | <2 | 17.923 |  |  | 10:30 | R Davis
2016-11-15 | 2016-11-21 | <2 | <2 | 23.799 |  |  | 15:30 | R Davis
2016-12-08 | 2016-12-14 | <2 | <2 | 29.867 |  |  | 10:00 | R Davis
2017-01-10 | 2017-01-17 | <2 | <2 | 39.168 |  |  | 8:00 | R Davis
2017-02-24 | 2017-03-07 | <2 | 4 | 32.656 |  |  | 8:00 | R Davis
2017-03-30 | 2017-04-07 | <2 | 2 | 30.699 |  |  | 8:00 | B Ford
2017-04-21 | 2017-04-27 | <2 | <2 | 19.711 |  |  | 9:00 | S Ledgard | 286.367 | Est. Total ML May 2016 to April 2017
2017-05-29 | 2017-06-06 | <2 | <2 | 18.599 |  |  | 10:00 | R Davis
2017-06-30 | 2017-07-10 | <2 | 3 | 16.789 |  |  | 10:00 | S Ledgard
2017-07-25 | 2017-08-01 | <2 | <2 | 17.26 |  |  | 8:00 | S Ledgard
2017-08-11 | 2017-08-18 | <2 | <2 | 17.3 |  |  | 10:00 | S Ledgard
2017-09-08 | 2017-09-15 | <2 | <2 | 19.1 |  |  | 8:00 | S Ledgard
2017-10-20 | 2017-03-11 | <2 | <2 | 24.8 |  |  | 8:30 | S Ledgard
2017-11-29 | 2017-05-12 | <2 | <2 | 23.18 |  |  | 8:30 | S Ledgard
2017-12-20 | 2018-01-10 | <2 | <2 | 26.23 |  |  | 3:30 | S.Ledgard
2018-01-24 | 2018-02-02 | <2 | <2 | 29.53 |  |  | 8:00 | S Ledgard
2018-02-23 | 2018-03-01 | <2 | <2 | 31.8 |  |  | 10:00 | R Davis
2018-03-26 | 2018-04-07 | <2 | <2 | 28.7 |  |  | 7:30 | R Davis
2018-04-20 | 2018-05-03 | <2 | <2 | 26.52 |  |  | 9:00 | R Davis | 279.808 | Est. Total ML May 2017 to April 2018
2018-05-18 | 2018-05-29 | <2 | <2 | 19.28 |  |  | 8:00 | R Davis | No 1 Lagoon sample
2018-06-29 | 2018-07-14 | <2 | <2 | 19.14 |  |  | 8:30 | S Ledgard | No 1 Lagoon sample
2018-07-18 | 2018-07-30 | <2 | <2 | 18.25 |  |  | 8:00 | S Ledgard | No 1 Lagoon sample
2018-08-10 | 2018-08-27 | <2 | <2 | 19.6 |  |  | 10:15 | B Ford | No 1 Lagoon sample
2018-09-21 | 2018-10-04 | <2 | <2 | 23.5 |  |  | 9:00 | B Ford | No 1 Lagoon sample
2018-10-29 | 2018-11-07 | <2 | 23 | 26.5 |  |  | 8:00 | B Ford | No 1 Lagoon sample
2018-11-30 | 2018-12-13 | <2 | <2 | 27.8 |  |  | 8:30 | B Ford | No 1 Lagoon sample
2018-12-19 | 2019-01-11 | <2 | <2 | 34.5 |  |  | 9:30 | S Ledgard | No 1 Lagoon sample
2019-01-31 | 2019-02-08 | 6 | <2 | 40.71 |  |  | 8:00 | S Ledgard | No 1 Lagoon sample
2019-02-22 | 2019-03-08 | <2 | <2 | 31.4 |  |  | 9:00 | R Davis | No 1 Lagoon sample
2019-03-29 | 2019-04-08 | <2 | <2 | 27.5 |  |  | 9:00 | S Ledgard | No 1 Lagoon sample
2019-04-23 | 2019-05-09 | <2 | <2 | 22.2 |  |  | 12:00 | R Davis | 310.38 | Est. Total ML May 2018 to April 2019
2019-05-22 | 2019-05-30 | <2 | <2 | 20.4 |  |  | 12:00 | R Davis | No 2 Lagoon sample
2019-06-24 | 2019-07-04 | <2 | 2 | 17.8 |  |  | 8:30 | S Ledgard | No 2 Lagoon sample
2019-07-26 | 2019-08-02 | <2 | <2 | 19.1 |  |  | 8:30 | R Davis | No 2 Lagoon sample
2019-08-26 | 2019-09-03 | <2 | 9 | 21.8 |  |  | 10:30 | S Ledgard | No 2 Lagoon sample
2019-09-06 | 2019-09-19 | 10 | <2 | 20.2 |  |  | 8:30 | S Ledgard | No 2 Lagoon sample
2019-10-18 | 2019-10-24 | <2 | <2 | 29.2 |  |  | 8:30 | R Davis | No 2 Lagoon sample
25/11/109 | 2019-12-10 | <2 | <2 | 30.5 |  |  | 8:30 | B Ford | No 2 Lagoon sample
2019-12-18 | 2020-01-10 | <2 | 4 | 40.8 |  |  | 13:00 | R Davis | No 2 Lagoon sample
2020-01-29 | 2020-02-07 | <2 | <2 | 37.6 |  |  | 9:00 | T Corby | No 2 Lagoon sample |  | 237.4 | total ML no.2
2020-02-21 | 2020-03-03 | <2 | <2 | 28.9 |  |  | 8:30 | S Ledgard | No 1 Lagoon sample
2020-03-30 | 2020-04-17 | <2 | <2 | 24.5 |  |  | 8:00 | S Ledgard | No 1 Lagoon sample
2020-04-27 | 2020-05-12 | <2 | <2 | 17.4 |  |  | 7:30 | R Davis | No 1 Lagoon sample
2020-05-28 | 2020-06-09 | <2 | <2 | 17 |  |  | 9:30 | R Davis | No 1 Lagoon sample
2020-06-26 | 2020-07-04 | <2 | 2 | 15.6 |  |  | 8:30 | S Ledgard | No 1 Lagoon sample
2020-07-31 | 2020-08-18 | <2 | <2 | 20.6 |  |  | 11:30 | B Ford | No 1 Lagoon sample
2020-08-21 | 2020-09-14 | <2 | 4 | 18.6 |  |  | 9:30am | R Davis | No 1 Lagoon sample
2020-09-29 | 2020-10-16 | <2 | <2 | 16.6 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2020-10-27 | 2021-11-12 | <2 | <2 | 20.3 |  |  | 10:00am | S Ledgard | No 1 Lagoon sample
2020-11-19 | 2020-12-03 | <2 | 5 | 21.1 |  |  | 10:00am | B Ford | No 1 Lagoon sample
2020-12-10 | 2021-01-07 | <2 | <2 | 29.6 |  |  | 10:00am | R Davis | No 1 Lagoon sample
2021-01-22 | 2021-02-22 | <2 | 4 | 31.8 |  |  | 8:30am | R Davis | No 1 Lagoon sample
2021-02-24 | 2021-03-26 | <2 | 5 | 20 |  |  | 8:30am | R Davis | No 1 Lagoon sample
2021-03-26 | 2021-04-14 | <2 | <2 | 22.1 |  |  | 9:00am | C Breen | No 1 Lagoon sample
2021-04-23 | 2021-05-12 | <2 | <2 | 19.9 |  |  | 12:00pm | T Corby | No 1 Lagoon sample |  | 253.2 | May to Apr
2021-05-28 | 2021-06-18 | <2 | <2 | 20.7 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2021-06-29 | 2021-07-14 | <2 | <2 | 18.1 |  |  | 8:30am | R Davis | No 2 Lagoon sample |  | C/over 9/6/21 | 40.6
2021-07-26 | 2021-08-17 | <2 | <2 | 18.8 |  |  | 11:30am | T Corby | No 2 Lagoon sample
2021-08-21 | 2021-09-20 | <2 | <2 | 19.6 |  |  | 9:00am | B Ford | No 2 Lagoon sample
2021-09-30 | 2021-10-14 | <2 | 2 | 20.26 |  |  | 9:00am | S Ledgard | No 2 Lagoon sample
2021-10-29 | 2021-11-09 | <2 | 2 | 18.7 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2021-12-09 | 2021-12-22 | <2 | <2 | 18.37 |  |  | 8:30am | B Ford | No 2 Lagoon sample
2021-12-20 | 2022-01-24 | <2 | <2 | 23.28 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2022-01-28 | 2022-03-04 | <2 | <2 | 24.36 |  |  | 10:30am | S Ledgard | No 2 Lagoon sample
2022-03-02 | 2022-04-07 | 3 | <2 | 23.11 |  |  | 8:00am | S Ledgard | No 2 Lagoon sample
2022-03-22 | 2022-04-07 | <2 | <2 | 34.34 |  |  | 9:30am | B Ford | No 2 Lagoon sample
2022-04-29 | 2022-05-20 | <2 | <2 | 19.76 |  |  | 10:00am | R Davis | No 2 Lagoon sample |  | 238.68 | 259.38 | Total YR
2022-05-26 | 2022-06-08 | <2 | <2 | 20.59 |  |  | 8:00am | R Davis | No 2 Lagoon sample
2022-06-21 | 2022-06-30 | <2 | <2 | 19.88 |  |  | 9:00am | B Ford | No 2 Lagoon sample
2022-07-28 | 2022-08-09 | <2 | <2 | 18.31 |  |  | 10:00am | S Ledgard | No 2 Lagoon sample
2022-08-31 | 2022-09-07 | 16 | 2 | 18.75 |  |  | 8:00am | S Ledgard | No 2 Lagoon sample
2022-09-26 | 2022-10-13 | <2 | <2 | 17.7 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2022-10-20 | 2022-11-02 | <2 | <2 | 18.4 |  |  | 10:00am | B Ford | No 2 Lagoon sample
2022-11-24 | 2022-12-02 | 7 | <2 | 18.8 |  |  | 10:00am | S Ledgard | No 2 Lagoon sample
2022-12-15 | 2023-01-20 | <2 | <2 | 27.4 |  |  | 7:30am | R Davis | No 2 Lagoon sample
2023-01-30 | 2023-02-08 | <2 | 5 | 31.4 |  |  | 8:30am | B Ford | No 2 Lagoon sample |  | 191.23
2023-03-03 | 2023-03-21 | <2 | <2 | 29.6 |  |  | 9:00am | B Ford | No 1 Lagoon sample |  | changed over 6/2/23
2023-03-27 | 2023-04-14 | <2 | <2 | 26.3 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2023-04-28 | 2023-05-12 | <2 | <2 | 19.1 |  |  | 8:00am | S Ledgard | No 1 Lagoon sample |  | 75 | 266.23 | Total
(BOD) | biochemical oxygen demand
(TSS) | total suspended solids
Maximum daily discharge for the month in kilolitres
L3 Concentration limits
Pollutant | Units of measure | 100 percentile Concentration Limit
BOD | milligrams per litre | 30
TSS | milligrams per litre | 30
L4 Volume and mass limits
Point | Units of measure | Volume/Mass Limit
1 | megalitre per year | 1000