## calc
Jugiong Sludge Lagoons
Raw Water
|  |  |  | Total | Ave | Days |  | lagoon calc. Ml |  |  |  |  | KL | plus cleaning | lagoon calc. Ml
|  |  | 2017-08-01 | 227665 | 8125 | 31 | X 557 | 17.26
[7 empty] | 1001-5000 | 5001-10000 | 10001-15000 | 15001-20000 | 20001-25000 | 25000+
|  |  | 2017-09-01 | 258000 | 8600 | 30 | 4 | 16 | 10 |  |  |  | 19148 |  | 19.148
|  |  | 2017-10-01 |  |  | 31 | 4 | 10 | 15 | 2 |  |  | 22828 | 2000 | 24.828 | Plus drained clarifier 10/10/17 2ML
|  |  | 2017-11-01 |  |  | 30 | 1 | 9 | 20 |  |  |  | 23182 |  | 23.182
|  |  | 2017-12-01 |  | 11727 | 31 | 3 | 5 | 18 | 5 |  |  | 26233 |  | 26.233
|  |  | 2018-01-01 | 418686 | 13506 | 31 |  | 6 | 15 | 10 |  |  | 29532 |  | 29.532
|  |  | 2018-02-01 | 417452 | 14909 | 28 |  | 1 | 10 | 16 | 1 |  | 31799 |  | 31.799
|  |  | 2018-03-01 | 392646 | 12666 | 31 |  | 5 | 19 | 7 |  |  | 28700 |  | 28.7
|  |  | 2018-04-01 | 366150 | 12205 | 30 | 1 | 6 | 17 | 6 |  |  | 26521 |  | 26.521
|  |  | 2018-05-01 | 272986 | 8806 | 31 | 2 | 20 | 9 |  |  |  | 19826 |  | 19.826
|  |  | 2018-06-01 | 224940 | 7498 | 30 | 4 | 22 | 4 |  |  |  | 17138 | 2000 | 19.138 | Plus drained clarifier 26/6/18 2ML
|  |  | 2018-07-01 | 251968 | 8128 | 31 | 3 | 23 | 5 |  |  |  | 18258 |  | 18.258
|  |  | 2018-08-01 | 256928 | 8288 | 31 | 3 | 19 | 9 |  |  |  | 19598 |  | 19.598
|  |  | 2018-09-01 | 297600 | 9920 | 30 | 1 | 14 | 15 |  |  |  | 21507 | 2000 | 23.507 | Plus drained clarifier 26/6/18 2ML
|  |  | 2018-10-01 | 388399 | 12529 | 31 |  | 6 | 13 | 9 |  |  | 26467 |  | 26.467
|  |  | 2018-11-01 | 378750 | 12625 | 30 | 2 | 5 | 16 | 5 | 2 |  | 27772 |  | 27.772
|  |  | 2018-12-01 | 469929 | 15159 | 31 | 1 | 1 | 12 | 15 | 2 |  | 34457 |  | 34.457
|  |  | 2019-01-01 | 536083 | 17293 | 31 |  | 2 | 5 | 17 | 6 | 1 | 40714 |  | 40.714
|  |  | 2019-02-01 | 410480 | 14660 | 28 |  | 3 | 13 | 8 | 3 | 1 | 31400 |  | 31.4
|  |  | 2019-03-01 | 388337 | 12527 | 31 | 2 | 4 | 19 | 6 |  |  | 27520 |  | 27.52
|  |  | 2019-04-01 | 313230 | 10441 | 30 | 1 | 12 | 17 |  |  |  | 22177 |  | 22.177
|  |  | 2019-05-01 | 261547 | 8437 | 31 | 4 | 16 | 11 |  |  |  | 20040 |  | 20.04
|  |  | 2019-06-01 | 243600 | 8120 | 30 | 4 | 20 | 6 |  |  |  | 17808 |  | 17.808
|  |  | 2019-07-01 | 244311 | 7881 | 31 | 7 | 15 | 8 | 1 |  |  | 19075 |  | 19.075
|  |  | 2019-08-01 | 238576 | 7696 | 31 | 8 | 16 | 7 |  |  |  | 17788 | 4000 | 21.788 | Cleaned both clarifiers 5/8, 20/8
|  |  | 2019-09-01 | 276120 | 9204 | 30 | 2 | 16 | 12 |  |  |  | 20274 |  | 20.274
|  |  | 2019-10-01 | 393700 | 12700 | 31 | 3 | 5 | 13 | 8 | 2 |  | 29268 |  | 29.268
|  |  | 2019-11-01 | 421950 | 14065 | 30 | 1 | 3 | 15 | 9 | 2 |  | 30561 |  | 30.561
|  |  | 2019-12-01 | 557969 | 17999 | 31 |  | 1 | 5 | 18 | 7 |  | 40857 |  | 40.857
|  |  | 2020-01-01 | 506013 | 16323 | 31 | 1 | 1 | 8 | 16 | 5 |  | 37648 |  | 37.648
|  |  | 2020-02-01 | 399562 | 13778 | 29 | 1 | 6 | 9 | 12 | 1 |  | 28897 |  | 28.897 | 4/2/20 lagoon change over
|  |  | 2020-03-01 | 339698 | 10958 | 31 |  | 13 | 15 | 3 |  |  | 24464 |  | 24.464
|  |  | 2020-04-01 | 237930 | 7931 | 30 | 6 | 18 | 6 |  |  |  | 17352 |  | 17.352
|  |  | 2020-05-01 | 221619 | 7149 | 31 | 4 | 25 | 2 |  |  |  | 17025 |  | 17.025
|  |  | 2020-06-01 | 207099 | 6903.3 | 30 | 8 | 20 | 2 |  |  |  | 15556 |  | 15.556
|  |  | 2020-07-01 | 225432 | 7272 | 31 | 4 | 25 | 6 |  |  |  | 20593 |  | 20.593
|  |  | 2020-08-01 | 225060 | 7260 | 31 | 7 | 21 | 3 |  |  |  | 16676 | 2000 | 18.676 | 2020-08-10 | cleaned clarifier
|  |  | 2020-09-01 | 223620 | 7454 | 30 | 8 | 17 | 5 |  |  |  | 16561 |  | 16.561
|  |  | 2020-10-01 | 236913 | 7642.3548 | 31 | 6 | 19 | 5 | 1 |  |  | 18298 | 2000 | 20.298 | 2020-10-27 | cleaned clarifier
|  |  | 2020-11-01 | 281897 | 9396.5667 | 30 | 2 | 16 | 10 | 2 |  |  | 21052 |  | 21.052
|  |  | 2020-12-01 | 385081 | 12421.9677 | 31 |  | 5 | 18 | 7 | 1 |  | 29634 |  | 29.634
|  |  | 2021-01-01 | 425429 | 13723.5161 | 31 | 1 | 5 | 10 | 14 | 1 |  | 31794 |  | 31.794
|  |  | 2021-02-01 | 265020 | 9465 | 28 | 4 | 11 | 12 |  | 1 |  | 19973 |  | 19.973 | 3/2/21 sludge removal no2.
|  |  | 2021-03-01 | 292268 | 9428 | 31 | 1 | 15 | 15 |  |  |  | 22064 |  | 22.064
|  |  | 2021-04-01 | 260280 | 8676 | 30 | 5 | 12 | 13 |  |  |  | 19925 |  | 19.925
|  |  | 2021-05-01 | 263972 | 8515.2258 | 31 | 6 | 14 | 8 | 3 |  |  | 20751 |  | 20.751
|  |  | 2021-06-01 | 247036 | 8234.5333 | 30 | 4 | 19 | 7 |  |  |  | 18143 |  | 18.143
|  |  | 2021-07-01 | 238510 | 7693.871 | 31 | 7 | 16 | 7 | 1 |  |  | 18740 |  | 18.74
|  |  | 2021-08-01 | 233936 | 7546.3226 | 31 | 9 | 15 | 7 |  |  |  | 17560 | 2000 | 19.56 | 2021-08-23 | cleaned clarifier
|  |  | 2021-09-01 | 229103 | 7636.7667 | 30 | 2 | 22 | 6 |  |  |  | 18264 | 2000 | 20.264 | 2021-09-27 | cleaned clarifier
|  |  | 2021-10-01 | 249942 | 8062.6452 | 31 | 4 | 20 | 7 |  |  |  | 18700 |  | 18.7
|  |  | 2021-11-01 | 250920 | 8364 | 30 | 3 | 20 | 7 |  |  |  | 18371 |  | 18.371
|  |  | 2021-12-01 | 314219 | 10136.0968 | 31 | 1 | 16 | 10 | 4 |  |  | 23285 |  | 23.285
|  |  | 2022-01-01 | 321861 | 10382.6129 | 31 | 4 | 14 | 5 | 7 | 1 |  | 24367 |  | 24.367
|  |  | 2022-02-01 | 315893 | 11281.8929 | 28 | 1 | 12 | 8 | 7 |  |  | 23116 |  | 23.116
|  |  | 2022-03-01 | 336064 | 10840.7742 | 31 | 2 | 10 | 16 | 3 |  |  | 24343 |  | 24.343
|  |  | 2022-04-01 | 280685 | 9356.1667 | 30 | 3 | 17 | 9 | 1 |  |  | 19765 |  | 19.765
|  |  | 2022-05-01 | 271410 | 8755.1613 | 31 | 5 | 15 | 9 | 2 |  |  | 20590 |  | 20.59
|  |  | 2022-06-01 | 238530 | 7951 | 30 | 10 | 10 | 6 | 3 | 1 |  | 19881 |  | 19.881
|  |  | 2022-07-01 | 243810 | 7864.8387 | 31 | 3 | 24 | 3 | 1 |  |  | 18312 |  | 18.312
|  |  | 2022-08-01 | 243630 | 7859.0323 | 31 | 4 | 21 | 5 | 1 |  |  | 18754 |  | 18.754 | cleaned clarifier no1,23/8/22
|  |  | 2022-09-01 | 239010 | 7967 | 30 | 3 | 22 | 5 |  |  |  | 17701 |  | 17.701
|  |  | 2022-10-01 | 248530 | 8017.0968 | 31 | 7 | 17 | 6 | 1 |  |  | 18405 |  | 18.405
|  |  | Nov-22 | 236460 | 7882 | 30 | 9 | 11 | 8 | 2 |  |  | 18786 |  | 18.786
|  |  | 2022-12-01 | 365960 | 11805.1613 | 31 | 1 | 7 | 15 | 6 | 1 |  | 27120 |  | 27.12 | sludge removal no1.
|  |  | 2023-01-01 | 441100 | 14229.0323 | 31 | 2 | 6 | 11 | 8 | 4 |  | 31364 |  | 31.364
|  |  | 2023-02-01 | 410940 | 13698 | 30 |  | 6 | 9 | 10 | 3 |  | 29658 |  | 29.658 | Lagoon change over 6th Feb
|  |  | 2023-03-01 | 355160 | 11456.7742 | 31 | 6 | 5 | 12 | 7 | 1 |  | 26256 |  | 26.256
|  |  | 2023-04-01 | 249070 | 8302.3333 | 30 | 6 | 14 | 9 | 1 |  |  | 19081 |  | 19.081
|  |  | 2023-05-01 | 253950 | 8191.9355 | 31 | 7 | 12 | 12 |  |  |  | 19691 |  | 19.691
RW Output Range (kL) |  | Waste (kL) | 2023-06-01 | 225610 | 7520.3333 | 30 | 5 | 20 | 3 | 2 |  |  | 16742 |  | 16.742
0 | 1000 | 30 | 2023-07-01 | 243370 | 7850.6452 | 31 | 7 | 16 | 7 | 1 |  |  | 18740 |  | 18.74
1001 | 5000 | 329 | 2023-08-01 | 235910 | 7610 | 31 | 8 | 12 | 10 | 1 |  |  | 19517 |  | 19.517
5001 | 10000 | 557 | 2023-09-01 | 298570 | 9952.3333 | 30 | 5 | 7 | 15 | 3 |  |  | 22767 | 2000 | 24.767 | cleaned clarifier no1,13/9/22
10001 | 15000 | 892 | 2023-10-01 | 329070 | 10615.1613 | 31 | 1 | 9 | 21 |  |  |  | 24074 | 2000 | 26.074 | cleaned clarifier no2,
15001 | 20000 | 1281 | 2023-11-01 | 380550 | 12685 | 30 | 3 | 5 | 12 | 9 | 1 |  | 27831 |  | 27.831
20001 | 25000 | 1826 | 2023-12-01 | 339630 | 10955.8065 | 31 | 1 | 15 | 12 | 2 | 1 |  | 23776 |  | 23.776
25001 | & over | 2407 | 2024-01-01 | 318800 | 10283.871 | 31 | 1 | 13 | 16 | 1 |  |  | 23123 |  | 23.123
|  |  | 2024-02-01 | 376310 | 12976.2069 | 29 | 1 | 7 | 8 | 13 |  |  | 28017 |  | 28.017
|  |  | 2024-03-01 | 432600 | 13954.8387 | 31 |  | 7 | 10 | 12 | 2 |  | 31843 |  | 31.843
|  |  | 2024-04-01 | 294608 | 9820.2667 | 30 | 1 | 16 | 12 | 1 |  |  | 21226 |  | 21.226 |  | 285021
|  |  | 2024-05-01 | 303100 | 9777.4194 | 31 | 1 | 14 | 16 |  |  |  | 22399 |  | 22.399 | WB52c | 285.021
|  |  | 2024-06-01 | 273890 | 9130 | 30 | 5 | 9 | 14 | 2 |  |  | 21708 |  | 21.708
|  |  | 2024-07-01 | 258820 | 8349.0323 | 31 | 6 | 12 | 12 |  |  |  | 19362 | 2000 | 21.362
|  |  | 2024-08-01 | 300030 | 9678.3871 | 31 | 1 | 14 | 16 |  |  |  | 22399 | 2000 | 24.399
|  |  | 2024-09-01 | 325536 | 10851.2 | 30 | 1 | 10 | 16 | 3 |  |  | 24014 |  | 24.014
|  |  | 2024-10-01 | 360359 | 11624.4839 | 31 |  | 6 | 23 | 2 |  |  | 26420 |  | 26.42
|  |  | 2024-11-01 | 461202 | 15373.4 | 30 | 1 | 1 | 8 | 18 | 2 |  | 34732 |  | 34.732
|  |  | 2024-12-01 | 447396 | 14432.129 | 31 |  | 6 | 8 | 16 | 1 |  | 32800 |  | 32.8
|  |  | 2025-01-01 | 526210 | 16974.5161 | 31 | 1 | 1 | 7 | 11 | 11 |  | 41307 |  | 41.307
|  |  | 2025-02-01 | 458737 | 16383.4643 | 28 | 1 | 1 | 7 | 10 | 9 |  | 36374 |  | 36.374
|  |  | 2025-03-01 | 483537 | 15597.9677 | 31 |  | 1 | 15 | 12 | 2 | 1 | 35368 |  | 35.368
|  |  | 2025-04-01 | 414763 | 13825.4333 | 30 |  | 1 | 19 | 10 |  |  | 30315 |  | 30.315

## 24_25 Discharge Summary
Date sample taken | Date report issued | BOD mg/l | TSS mg/l | Estimated Monthly Discharge ML | Daily maximum discharge for the month in kl | EPA REF | Time Sample Collected | Name of collecting officer | Monitoring Point | Comments
2024-05-29 | 2024-06-20 | <2 | <2 | 22.399 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2024-06-19 | 2024-07-15 | <2 | <2 | 22 |  |  | 7:30am | S Ledgard | No 2 Lagoon sample
2024-07-25 | 2024-08-16 | <2 | <2 | 21.362 |  |  |  |  | No 2 Lagoon sample | Number 2 Clarifier Cleaning
2024-08-05 | 2024-08-28 | <2 | <2 | 24.399 |  |  |  |  | No 2 Lagoon sample | Number 1 clarifier cleaning
2024-09-01 |  |  |  | 24.014 |  |  |  |  | No 2 Lagoon sample | * No sample taken due to the retirement of staff member
2024-10-01 |  |  |  | 26.42 |  |  |  |  | No 2 Lagoon sample | * No sample taken due to the retirement of staff member
2024-11-01 |  |  |  | 34.732 |  |  |  |  | No 2 Lagoon sample | * No sample taken due to the retirement of staff member
2024-12-01 |  |  |  | 32.8 |  |  |  |  | No 2 Lagoon sample | * No sample taken due to the retirement of staff member
2025-01-01 |  |  |  | 41.307 |  |  |  |  | No 2 Lagoon sample | * No sample taken due to the retirement of staff member
2025-02-21 | 2025-03-13 | <2 | <2 | 36.374 |  |  | 10.15am | WTO Operator | No 2 Lagoon sample
2025-03-24 | 2025-04-10 | <2 | <2 | 35.368 |  |  | 8.30am | WTO Operator | No 2 Lagoon sample
2025-04-01 |  |  |  | 30.315 |  |  |  |  | No 2 Lagoon sample
|  |  |  | 351.49 | Total Discharge
|  |  |  | 22.399 | Total Discharge Lagoon No. 1
|  |  |  | 329.091 | Total Discharge Lagoon No. 2
|  |  |  | 12 | Number of Measurments taken

## Historical
Date sample taken | Date report issued | BOD mg/l | TSS mg/l | Estimated Monthly Discharge ML | Daily maximum discharge for the month in kl | EPA REF | Time Sample Collected | Name of collecting officer
24/1/18 | 2018-02-02 | <2 | <2 | 29.53 |  |  | 8am | S Ledgard
23/2/18 | 2018-01-03 | <2 | <2 | 31.8 |  |  | 10am | R Davis
26/3/18 | 2018-07-04 | <2 | <2 | 28.7 |  |  | 7:30am | R Davis
20/4/18 | 2018-03-05 | <2 | <2 | 26.52 |  |  | 9am | R Davis
18/5/18 | 29/5/18 | <2 | <2 | 19.82 |  |  | 8:00am | R Davis | No 1 Lagoon sample
29/6/18 | 14/7/18 | <2 | <2 | 19.14 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
18/7/18 | 30/7/18 | <2 | <2 | 18.25 |  |  | 8:00am | S Ledgard | No 1 Lagoon sample
2018-08-10 | 2018-08-27 | <2 | <2 | 19.6 |  |  | 10:15am | B Ford | No 1 Lagoon sample
2018-09-21 | 2018-10-04 | <2 | <2 | 23.5 |  |  | 9:00am | B Ford | No 1 Lagoon sample
2018-10-29 | 2018-11-07 | <2 | 23 | 26.5 |  |  | 8:00am | B Ford | No 1 Lagoon sample
2018-11-30 | 2018-12-13 | <2 | <2 | 27.8 |  |  | 8:30am | B Ford | No 1 Lagoon sample
2018-12-19 | 2019-01-11 | <2 | <2 | 34.5 |  |  | 9:30am | S Ledgard | No 1 Lagoon sample
2019-01-31 | 2019-02-08 | 6 | <2 | 40.7 |  |  | 8:00am | S Ledgard | No 1 Lagoon sample
2019-02-22 | 2019-03-08 | <2 | <2 | 31.4 |  |  | 9:00am | R Davis | No 1 Lagoon sample
2019-03-29 | 2019-04-08 | <2 | <2 | 27.5 |  |  | 9:00am | S Ledgard | No 1 Lagoon sample
2019-04-23 | 2019-05-09 | <2 | <2 | 22.2 |  |  | 12:00pm | R Davis | 310.91 | total for the 12months
2019-05-22 | 2019-05-30 | <2 | <2 | 20.4 |  |  | 12:00pm | R Davis | No 2 Lagoon sample
2019-06-24 | 2019-07-04 | <2 | 2 | 17.8 |  |  | 8:30am | S Ledgard | No 2 Lagoon sample
2019-07-26 | 2019-08-02 | <2 | <2 | 19.1 |  |  | 8:30am | R Davis | No 2 Lagoon sample
2019-08-26 | 2019-09-03 | <2 | 9 | 21.8 |  |  | 10:30am | S Ledgard | No 2 Lagoon sample
2019-09-06 | 2019-09-19 | 10 | <2 | 20.2 |  |  | 8:30am | S Ledgard | No 2 Lagoon sample
2019-10-18 | 2019-10-24 | <2 | <2 | 29.2 |  |  | 8:30am | R Davis | No 2 Lagoon sample
2019-11-25 | 2019-12-10 | <2 | <2 | 30.5 |  |  | 8:30am | B Ford | No 2 Lagoon sample
2019-12-18 | 2020-01-10 | <2 | 4 | 40.8 |  |  | 1pm | R Davis | No 2 Lagoon sample
2020-01-29 | 2020-02-07 | <2 | <2 | 37.6 |  |  | 9:00am | T Corby | No 2 Lagoon sample |  | 237.4
2020-02-21 | 2020-03-03 | <2 | <2 | 28.9 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2020-03-30 | 2020-04-17 | <2 | <2 | 24.5 |  |  | 8:00am | S Ledgard | No 1 Lagoon sample
2020-04-27 | 2020-05-12 | <2 | <2 | 17.4 |  |  | 7:30am | R Davis | No 1 Lagoon sample
2020-05-28 | 2020-06-09 | <2 | <2 | 17 |  |  | 9:30am | R Davis | No 1 Lagoon sample
2020-06-26 | 2020-07-04 | <2 | 2 | 15.6 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2020-07-31 | 2020-08-18 | <2 | <2 | 20.6 |  |  | 11:30am | B Ford | No 1 Lagoon sample
2020-08-21 | 2020-09-14 | <2 | 4 | 18.6 |  |  | 9:30am | R Davis | No 1 Lagoon sample
2020-09-29 | 2020-10-16 | <2 | <2 | 16.6 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2020-10-27 | 2021-11-12 | <2 | <2 | 20.3 |  |  | 10:00am | S Ledgard | No 1 Lagoon sample
2020-11-19 | 2020-12-03 | <2 | 5 | 21.1 |  |  | 10:00am | B Ford | No 1 Lagoon sample
2020-12-10 | 2021-01-07 | <2 | <2 | 29.6 |  |  | 10:00am | R Davis | No 1 Lagoon sample
2021-01-22 | 2021-02-22 | <2 | 4 | 31.8 |  |  | 8:30am | R Davis | No 1 Lagoon sample
2021-02-24 | 2021-03-26 | <2 | 5 | 20 |  |  | 8:30am | R Davis | No 1 Lagoon sample
2021-03-26 | 2021-04-14 | <2 | <2 | 22.1 |  |  | 9:00am | C Breen | No 1 Lagoon sample
2021-04-23 | 2021-05-12 | <2 | <2 | 19.9 |  |  | 12:00pm | T Corby | No 1 Lagoon sample |  | 253.2
2021-05-28 | 2021-06-18 | <2 | <2 | 20.7 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2021-06-29 | 2021-07-14 | <2 | <2 | 18.1 |  |  | 8:30am | R Davis | No 2 Lagoon sample |  | lagoon change over 9/6/21 |  |  | 40.6
2021-07-26 | 2021-08-17 | <2 | <2 | 18.74 |  |  | 11:30am | T Corby | No 2 Lagoon sample
2021-08-21 | 2021-09-20 | <2 | <2 | 19.56 |  |  | 9:00am | B Ford | No 2 Lagoon sample |  | drained clarifier 23/8
2021-09-30 | 2021-10-14 | <2 | 2 | 20.26 |  |  | 9:00am | S Ledgard | No 2 Lagoon sample |  | drained clarifier 27/9
2021-10-29 | 2021-11-09 | <2 | 2 | 18.7 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2021-12-09 | 2021-12-22 | <2 | <2 | 18.37 |  |  | 8:30am | B Ford | No 2 Lagoon sample
2021-12-20 | 2022-01-24 | <2 | <2 | 23.28 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2022-01-28 | 2022-03-04 | <2 | <2 | 24.36 |  |  | 10:30am | S Ledgard | No 2 Lagoon sample
2022-03-02 | 2022-04-07 | 3 | <2 | 23.11 |  |  | 8:00am | S Ledgard | No 2 Lagoon sample
2022-03-22 | 2022-04-07 | <2 | <2 | 34.34 |  |  | 9:30am | B Ford | No 2 Lagoon sample
2022-04-29 | 2022-05-20 | <2 | <2 | 19.76 |  |  | 10:00am | R Davis | No 2 Lagoon sample |  | 238.58
2022-05-26 | 2022-06-08 | <2 | <2 | 20.59 |  |  | 8:00am | R Davis | No 2 Lagoon sample
2022-06-21 | 2022-06-30 | <2 | <2 | 19.88 |  |  | 9:00am | B Ford | No 2 Lagoon sample
2022-07-28 | 2022-08-09 | <2 | <2 | 18.31 |  |  | 10:00am | S Ledgard | No 2 Lagoon sample
2022-08-31 | 2022-09-07 | 16 | 2 | 18.75 |  |  | 8:00am | S Ledgard | No 2 Lagoon sample |  | drained clarifier 23/8
2022-09-26 | 2022-10-13 | <2 | <2 | 17.7 |  |  | 8:00am | B Ford | No 2 Lagoon sample
2022-10-20 | 2022-11-02 | <2 | <2 | 18.4 |  |  | 10:00am | B Ford | No 2 Lagoon sample
2022-11-24 | 2022-12-02 | 7 | <2 | 18.8 |  |  | 10:00am | S Ledgard | No 2 Lagoon sample
2022-12-15 | 2023-01-20 | <2 | <2 | 27.4 |  |  | 7:30am | R Davis | No 2 Lagoon sample
2023-01-30 | 2023-02-08 | <2 | 5 | 31.4 |  |  | 8:30am | B Ford | No 2 Lagoon sample |  | 191.23
2023-03-03 | 2023-03-21 | <2 | <2 | 29.6 |  |  | 9:00am | B Ford | No 1 Lagoon sample |  | changed over 6/2/23
2023-03-27 | 2023-04-14 | <2 | <2 | 26.3 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2023-04-28 | 2023-05-12 | <2 | <2 | 19.1 |  |  | 8:00am | S Ledgard | No 1 Lagoon sample |  | 75 | 266.23 | Total
2023-05-23 | 2023-06-01 | <2 | <2 | 19 |  |  | 10:00am | S Ledgard | No 1 Lagoon sample
2023-06-28 | 2023-07-06 | <2 | 2 | 16.7 |  |  | 8:00am | R Davis | No 1 Lagoon sample
2023-07-26 | 2023-08-11 | 5 | <2 | 18.7 |  |  | 8:00am | R Davis | No 1 Lagoon sample
2023-08-31 | 2023-09-18 | <2 | <2 | 19 |  |  | 11:00am | S Ledgard | No 1 Lagoon sample
2023-09-25 | 2023-10-25 | 7 | <2 | 24.8 |  |  | 12:00pm | S Ledgard | No 1 Lagoon sample |  | drained clarifier 13/9
2023-10-31 | 2023-11-27 | <2 | <2 | 26 |  |  | 11:30am | S Ledgard | No 1 Lagoon sample |  | drained clarifier
2023-11-29 | 2023-12-14 | <2 | 2 | 27 |  |  | 8:30am | R Davis | No 1 Lagoon sample
2023-12-06 | 2023-12-21 | <2 | <2 | 23 |  |  | 9:00am | R Davis | No 1 Lagoon sample
2024-01-24 | 2024-02-14 | <2 | <2 | 23 |  |  | 9:00am | S Ledgard | No 1 Lagoon sample
2024-02-15 | 2024-03-15 | <2 | <2 | 28 |  |  | 9:00am | S Ledgard | No 1 Lagoon sample
2024-03-28 | 2024-05-02 | 7 | <2 | 31.8 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2024-04-24 | 2024-05-31 | <2 | <2 | 21 |  |  | 8:00am | R Davis | No 1 Lagoon sample |  |  | 278 | Total
2024-05-29 | 2024-06-20 | <2 | <2 | 22.399 |  |  | 8:30am | S Ledgard | No 1 Lagoon sample
2024-06-19 | 2024-07-15 | <2 | <2 | 22 |  |  | 7:30am | S Ledgard | No 2 Lagoon sample
2024-07-25 | 2024-08-16 | <2 | <2 | 21.362 |  |  |  |  | No 2 Lagoon sample |  | Number 2 Clarifier Cleaning
2024-08-05 | 2024-08-28 | <2 | <2 | 24.399 |  |  |  |  | No 2 Lagoon sample |  | Number 1 clarifier cleaning
2024-09-01 |  |  |  | 24.014 |  |  | No Sample Taken |  | No 2 Lagoon sample |  |  | * No sample taken due to the retirement of staff member
2024-10-01 |  |  |  | 26.42 |  |  | No Sample Taken |  | No 2 Lagoon sample |  |  | * No sample taken due to the retirement of staff member
2024-11-01 |  |  |  | 34.732 |  |  | No Sample Taken |  | No 2 Lagoon sample |  |  | * No sample taken due to the retirement of staff member
2024-12-01 |  |  |  | 32.8 |  |  | No Sample Taken |  | No 2 Lagoon sample |  |  | * No sample taken due to the retirement of staff member
2025-01-01 |  |  |  | 41.307 |  |  | No Sample Taken |  | No 2 Lagoon sample |  |  | * No sample taken due to the retirement of staff member
2025-02-21 | 2025-03-13 | <2 | <2 | 36.374 |  |  | 10.15am | WTO Operator | No 2 Lagoon sample
2025-03-24 | 2025-04-10 | <2 | <2 | 35.368 |  |  | 8.30am | WTO Operator | No 2 Lagoon sample
2025-04-21 | 2025-04-28 | <2 | <2 | 30.315 |  |  | 8.30am | WTO Operator | No 2 Lagoon sample |  |  | 351.49 | Total